## Start
FireFlow Ver 2.0
Project Description | Sears Backflow Retro Fit
Project Number
Address | 2050 Southgate Rd
Date of Flow test | 2018-07-31
(mm/dd/yy)
Inspector
(this button will clear all the information above)

## Hydrant
Enter the following pressure readings in the boxes below, then click on "Flow Curve"
| Input here! |  | You know the pitot flow but |  |  |  | Reduced Pressures
Static | 106 | psi | not the pressure? Enter it |  |  |  | Static | 95.4
here. If not, make sure you
Residual | 20 | psi | enter zero or leave blank! |  |  |  | Residual | 9.4
Pitot
Pitot | 0 | psi | Flow | 2600 | gpm |  | Pitot | 26.28 | ~
You are using the above flow!
Enter base of riser |  |  |  | Safety factor? |  |  |  | The Pitot Flow is: | 2600
system demand here |  |  |  | 10
Flow | 1730.89 | gpm | [5 empty] | Flow at 20 psi is: | 2600
Pressure | 53.607 | psi
This hydrant should be painted:
Flow orifice & Friction coefficient | [6 empty] | ~ | ~
enter diameter | 4.026 | in. | 0.83 |  |  |  | ~ | Blue
Define orifice characteristics: | [6 empty] | Hydrant : 893-R
2
The information under this line is for graphing purposes of the Water flow chart. Please to not modify!
Pres | Flow |  | Pres | Flow |  |  |  | 100% |  | 106
0 | 2910.7798 |  | 0 | 2749.7949 |  |  |  | 150% |  | 20
10 | 2759.1204 |  | 10 | 2590.1889 | [5 empty] | 2600
20 | 2600 |  | 20 | 2421.7244 |  |  |  | 20 | 2600 | 0.83
20 | 2600 |  | 17.35 | 2467.3204 |  |  |  | 20 | 2421.7244 | 1730.89
20 | 2600 |  | 14.7 | 2512.2097 |  |  |  | 20 | 2600 | 53.607
20 | 2600 |  | 12.05 | 2556.4259 |  |  | Play pipe
20 | 2600 |  | 9.4 | 2600 |  |  | Smooth |  | 1730.89 | 1250
41.5 | 2225.904 |  | 30.9 | 2225.904 |  |  | Square |  | 53.607 | 200
63 | 1788.2044 |  | 52.4 | 1788.2044 |  |  | Protruding |  |  | 170.4805
73.75 | 1530.912 |  | 63.15 | 1530.912
84.5 | 1229.8749 |  | 73.9 | 1229.8749 |  |  | 2½
95.25 | 845.8722 |  | 84.65 | 845.8722 |  |  | 4½
106 | 0 |  | 95.4 | 0 |  |  | 15
Other Private Contractor
[6 empty] | 1 | DEM | Doreen Moore, Fire Protection Engineer
[6 empty] | 2 | JAH | Jeff Hanenberg, Fire Code Inspector
[6 empty] | 3 | JEK | Jim Koehler, Fire Code Inspector
[6 empty] | 4 | JHS | John Shumaker, Fire Code Inspector
[6 empty] | 5 | JRW | Jay Weightman, Fire Code Inspector
[6 empty] | 6 | JXT | JR Trout, Fire Code Inspector
[6 empty] | 7 | JYP | Jacob Pulfer, Fire Code Inspector
[6 empty] | 8 | KAY | Kay Yeager, Hazmat Specialist
[6 empty] | 9 | KHJ | Kristen Johnson, Fire Code Inspector
[6 empty] | 10 | KLM | Kristen McClellan, Fire Protection Engineer
| Pump Curve calculations |  |  |  |  | 11 | RCE | Rhonda Embres, Fire Code Inspector
| 140% | 0 | 227.3333 | 0 |  | 12 | RSH | Robert Helton, Fire Code Inspector
| 100% | 100 | 170.4805 | 1250 |  | 13 | SDS | Steve Smith, Fire Protection Engineer
| 65% | 150 | 115.3601 | 1875 |  | 14 | WRD | Water Resources Department
|  |  | 106 |  |  | 15 | other | Other Private Contractor
83.8139
59.0268
1 | 25 |  | 13
2 | 50 |  | 1250
3 | 100
4 | 150
5 | 200
6 | 250
7 | 300
8 | 400
9 | 450
10 | 500
11 | 750
12 | 1000
13 | 1250
14 | 1500
15 | 2000
16 | 2500
17 | 3000
18 | 3500
19 | 4000
20 | 4500
21 | 5000

## Pump
Pump Information
Rated Pump Capacity |  | Inlet Pipe Diameter
1250 | gpm | 8 | inches
Rated Net Pressure |  | Outlet Pipe Diameter
200 | feet | 6 | inches | Percentage of Rated Capacity
Converted Net Head |  | Other Pipe Diameters |  | 2
56.3333 | psi | 6 | inches
Velocity at inlet |  | Other Velocities
11.9669 | ft/s | 21.2746 | ft/s
~ |  | Velocity may be too high!
Flow Being used |  | Velocity head
1875 | gpm | 2.2258 | feet of H2O
|  | 0.96451 | psi
based on the assumption that 150% of the rated capacity will produce 65% rated head